## Sch 1_Central
Sl. No. | Name of DRTB centre | State | Zone | Different sections of the DRTB centre (as written in checklist) | Updated Section labels | Facility Length (in feet) | Facility Width (in feet) | Facility Height (in feet) | Total facility area (in sqft) | Total facility volume (in cubic feet) | Total facility volume (in cubic meter) | Total volumetric doses (12mW/m3) (in Watt) | Fixture output (___0.4W__) Number | Fixture output (___0.9W__) Number | Fixture output (___1.21 W__) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Total no of fixtures proposed (T=N+O+P+Q+R+S) | Remarks
1 | Bheemrao Ambedkar Hospital & JNMC, Raipur | Chhattisgarh | Central | TB OPD WAITING AREA | OPD/ Waiting area | 27.6 | 28.5 | 10.7 | 786.6 | 8416.62 | 238.3321 | 2.86 | 1 | 1 | 1 |  |  |  | 3
1 | Bheemrao Ambedkar Hospital & JNMC, Raipur | Chhattisgarh | Central | FEMALE DRTB WARD | DR TB Wards | 35.9 | 17.85 | 10.3 | 640.815 | 6600.3945 | 186.9024 | 2.2428
1 | Bheemrao Ambedkar Hospital & JNMC, Raipur | Chhattisgarh | Central | MALE DRTB WARD | DR TB Wards | 35 | 17.85 | 10.3 | 624.75 | 6434.925 | 182.2168 | 2.1866
2 | Chattisgarh Institute of Medical Sciences, Bilaspur | Chhattisgarh | Central | MALE & FEMALE DRTB WARD | DR TB Wards | 43.6 | 26 | 12.28 | 1133.6 | 13920.608 | 394.1877 | 4.7303
2 | Chattisgarh Institute of Medical Sciences, Bilaspur | Chhattisgarh | Central | REGISTRATION AREA | Registration/ waiting area | 20 | 14.5 | 9.5 | 290 | 2755 | 78.0129 | 0.93615
3 | Government Medical College Hospital Ambikapur(Sarguja) | Chhattisgarh | Central | DRTB female | DR TB Wards | 20 | 16 | 12.3 | 320 | 3936 | 111.4551 | 1.3375
3 | Government Medical College Hospital Ambikapur(Sarguja) | Chhattisgarh | Central | corridor area (OPD +X ray +DMC) | OPD/ Waiting area | 97 | 7.9 | 12.3 | 766.3 | 9425.49 | 266.9002 | 3.2028
3 | Government Medical College Hospital Ambikapur(Sarguja) | Chhattisgarh | Central | DRTB male | DR TB Wards | 23 | 20 | 12.3 | 460 | 5658 | 160.2167 | 1.9226
4 | Government TB Hospital, Nowgong, Chatarpur | Madhya Pradesh | Central | DRTB Male &Female combine Ward | DR TB Wards | 100 | 21.8 | 14 | 2180 | 30520 | 864.2302 | 10.3708
5 | Manorama Raje Tuberculosis Hospital, Indore | Madhya Pradesh | Central | DSTB Female Ward | DS TB Wards | 21.7 | 41 | 11.9 | 889.7 | 10587.43 | 299.8026 | 3.5976
5 | Manorama Raje Tuberculosis Hospital, Indore | Madhya Pradesh | Central | DSTB Male Ward | DS TB Wards | 21.7 | 41 | 11.9 | 889.7 | 10587.43 | 299.8026 | 3.5976
5 | Manorama Raje Tuberculosis Hospital, Indore | Madhya Pradesh | Central | DRTB Male Ward | DR TB Wards | 37.7 | 11.8 | 12.3 | 444.86 | 5471.778 | 154.9435 | 1.8593
5 | Manorama Raje Tuberculosis Hospital, Indore | Madhya Pradesh | Central | Bronchoscopy Unit | Bronchoscopy | 18.6 | 21.2 | 11 | 394.32 | 4337.52 | 122.8249 | 1.4739
6 | R. D. Gardi Medical College, Ujjain | Madhya Pradesh | Central | DRTB Male Ward | DR TB Wards | 57.4 | 22.2 | 11 | 1274.28 | 14017.08 | 396.9195 | 4.763
6 | R. D. Gardi Medical College, Ujjain | Madhya Pradesh | Central | DRTB Female Ward | DR TB Wards | 23.4 | 21.8 | 11 | 510.12 | 5611.32 | 158.8949 | 1.9067
7 | Regional Institute of Respiratory Disease, Bhopal | Madhya Pradesh | Central | Bronchoscopy suite | Bronchoscopy | 21 | 13.8 | 12.6 | 289.8 | 3651.48 | 103.3984 | 1.2408
7 | Regional Institute of Respiratory Disease, Bhopal | Madhya Pradesh | Central | DRTB Male &Female combine Ward | DR TB Wards | 107.7 | 32.5 | 10.8 | 3500.25 | 37802.7 | 1070.4533 | 12.8454
8 | Victoria Hospital, Jabalpur | Madhya Pradesh | Central | DSTB Male Ward | DS TB Wards | 34.8 | 29.7 | 15.5 | 1033.56 | 16020.18 | 453.641 | 5.4437
8 | Victoria Hospital, Jabalpur | Madhya Pradesh | Central | DRTB Male &Female combine Ward | DR TB Wards | 35 | 30.3 | 12.8 | 1060.5 | 13574.4 | 384.3842 | 4.6126
9 | Institute of respiratiory disease, Jaipur | Rajasthan | Central | Bronchoscopy Unit | Bronchoscopy | 21 | 19 | 10 | 399 | 3990 | 112.9842 | 1.3558
9 | Institute of respiratiory disease, Jaipur | Rajasthan | Central | DSTB Ward | DS TB Wards | 60 | 38 | 13 | 2280 | 29640 | 839.3113 | 10.0717
9 | Institute of respiratiory disease, Jaipur | Rajasthan | Central | DRTB Ward (Male) | DR TB Wards | 54 | 23 | 13 | 1242 | 16146 | 457.2038 | 5.4864
9 | Institute of respiratiory disease, Jaipur | Rajasthan | Central | DRTB Ward (Female) | DR TB Wards | 60 | 25 | 13 | 1500 | 19500 | 552.1785 | 6.6261
10 | New Medical College, Kota | Rajasthan | Central | Bronchoscopy Room | Bronchoscopy | 24 | 15 | 11.5 | 360 | 4140 | 117.2317 | 1.4068
10 | New Medical College, Kota | Rajasthan | Central | TB OPD | OPD/ Waiting area | 28.6 | 26.6 | 11.5 | 760.76 | 8748.74 | 247.7367 | 2.9728
10 | New Medical College, Kota | Rajasthan | Central | DSTB Area | DS TB Wards | 75 | 24 | 12 | 1800 | 21600 | 611.6439 | 7.3397
10 | New Medical College, Kota | Rajasthan | Central | DRTB area | DR TB Wards | 58 | 24 | 12 | 1392 | 16704 | 473.0046 | 5.6761
11 | Rabindranath Tagore Medical College, Udaipur | Rajasthan | Central | Bronchoscopy Unit | Bronchoscopy | 24 | 20 | 11 | 480 | 5280 | 149.513 | 1.7942
11 | Rabindranath Tagore Medical College, Udaipur | Rajasthan | Central | DSTB Ward (Female) | DS TB Wards | 120 | 28 | 14 | 3360 | 47040 | 1332.0245 | 15.9843
11 | Rabindranath Tagore Medical College, Udaipur | Rajasthan | Central | DSTB Ward (male) | DS TB Wards | 120 | 28 | 14 | 3360 | 47040 | 1332.0245 | 15.9843
11 | Rabindranath Tagore Medical College, Udaipur | Rajasthan | Central | Waiting area (OPD + Registration) | Registration/ waiting area | 33 | 10 | 14 | 330 | 4620 | 130.8238 | 1.5699
11 | Rabindranath Tagore Medical College, Udaipur | Rajasthan | Central | Waiting area (inside) | Registration/ waiting area | 25 | 33 | 14 | 825 | 11550 | 327.0596 | 3.9247
12 | S P Medical College, Bikaner | Rajasthan | Central | DRTB Ward (Female + Male) | DR TB Wards | 70 | 25 | 12 | 1750 | 21000 | 594.6538 | 7.1358
12 | S P Medical College, Bikaner | Rajasthan | Central | Bronchoscopy Unit | Bronchoscopy | 14 | 19 | 11 | 266 | 2926 | 82.8551 | 0.99426
13 | Banswada | Rajasthan | Central | DRTB Ward | DR TB Wards | 17.8 | 12.8 | 12 | 227.84 | 2734.08 | 77.4205 | 0.92905
13 | Banswada | Rajasthan | Central | DSTB Ward | DS TB Wards | 51.3 | 18 | 12 | 923.4 | 11080.8 | 313.7733 | 3.7653
14 | Bharatpur | Rajasthan | Central | DRTB Ward Male | DR TB Wards | 21.5 | 9.3 | 12.4 | 199.95 | 2479.38 | 70.2082 | 0.8425
14 | Bharatpur | Rajasthan | Central | DRTB Ward Female | DR TB Wards | 21.8 | 8.8 | 12.4 | 191.84 | 2378.816 | 67.3606 | 0.80833
14 | Bharatpur | Rajasthan | Central | TB OPD | OPD/ Waiting area | 19.4 | 18.5 | 12.4 | 358.9 | 4450.36 | 126.0202 | 1.5122
14 | Bharatpur | Rajasthan | Central | Bronchoscopy Unit | Bronchoscopy | 21.4 | 19.4 | 12.4 | 415.16 | 5147.984 | 145.7747 | 1.7493
15 | Jagdalpur | Chhattisgarh | Central | Preferred DRTB Ward | DR TB Wards | 27 | 22 | 9.7 | 594 | 5761.8 | 163.156 | 1.9579
15 | Jagdalpur | Chhattisgarh | Central | Preferred DSTB Ward | DS TB Wards | 27 | 22 | 9.7 | 594 | 5761.8 | 163.156 | 1.9579
15 | Jagdalpur | Chhattisgarh | Central | Preferred TB Ward | TB Ward | 27 | 22 | 9.7 | 594 | 5761.8 | 163.156 | 1.9579
15 | Jagdalpur | Chhattisgarh | Central | Bronchoscopy Room | Bronchoscopy | 22 | 13.5 | 9 | 297 | 2673 | 75.6909 | 0.90829
16 | Jhalawar | Rajasthan | Central | Proposed MALE DRTB Ward | DR TB Wards | 30 | 20 | 9.7 | 600 | 5820 | 164.804 | 1.9776
16 | Jhalawar | Rajasthan | Central | Proposed FEMALE DRTB Ward | DR TB Wards | 24 | 18 | 9.7 | 432 | 4190.4 | 118.6589 | 1.4239
17 | Bhilwara | Rajasthan | Central | TB ward | DS TB Wards | 57 | 20 | 12.5 | 1140 | 14250 | 403.5151 | 4.8422
17 | Bhilwara | Rajasthan | Central | DRTB Ward | DR TB Wards | 28 | 20 | 12.5 | 560 | 7000 | 198.2179 | 2.3786
17 | Bhilwara | Rajasthan | Central | OPD 1 | OPD/ Waiting area | 14 | 10 | 12.5 | 140 | 1750 | 49.5545 | 0.59465
17 | Bhilwara | Rajasthan | Central | OPD 2 | OPD/ Waiting area | 14 | 10 | 12.5 | 140 | 1750 | 49.5545 | 0.59465
17 | Bhilwara | Rajasthan | Central | OPD 3 | OPD/ Waiting area | 12 | 8.6 | 12.5 | 103.2 | 1290 | 36.5287 | 0.43834
17 | Bhilwara | Rajasthan | Central | Bronchoscopy | Bronchoscopy | 22 | 17 | 12.5 | 374 | 4675 | 132.3813 | 1.5886
18 | Pali | Rajasthan | Central | Mixed TB Ward | DS TB Wards | 111 | 27 | 10 | 2997 | 29970 | 848.6559 | 10.1839
18 | Pali | Rajasthan | Central | Existing Microscopy lab | TB lab | 15 | 10 | 15 | 150 | 2250 | 63.7129 | 0.76455
18 | Pali | Rajasthan | Central | Existing TB OPD | OPD/ Waiting area | 10 | 10 | 15 | 100 | 1500 | 42.4753 | 0.5097
18 | Pali | Rajasthan | Central | Bronchoscopy Room | Bronchoscopy | 33 | 14 | 10 | 462 | 4620 | 130.8238 | 1.5699
19 | Chhindwara | Madhya Pradesh | Central | DRTB Female + Male ward | DR TB Wards | 19.8 | 19.7 | 11 | 390.06 | 4290.66 | 121.498 | 1.458
19 | Chhindwara | Madhya Pradesh | Central | DSTB ward 1 | DS TB Wards | 25 | 20 | 11 | 500 | 5500 | 155.7427 | 1.8689
19 | Chhindwara | Madhya Pradesh | Central | Respiratory ward | Other | 30 | 19 | 11 | 570 | 6270 | 177.5466 | 2.1306
19 | Chhindwara | Madhya Pradesh | Central | Bronchoscopy Room | Bronchoscopy | 15 | 11 | 9 | 165 | 1485 | 42.0505 | 0.50461
19 | Chhindwara | Madhya Pradesh | Central | TB OPD | OPD/ Waiting area | 21 | 10 | 9 | 210 | 1890 | 53.5188 | 0.64223
20 | Jabalpur | Madhya Pradesh | Central | DSTB male ward | DS TB Wards | 52 | 21 | 12.8 | 1092 | 13977.6 | 395.8016 | 4.7496
20 | Jabalpur | Madhya Pradesh | Central | DSTB Female ward | DS TB Wards | 50 | 21 | 12.8 | 1050 | 13440 | 380.5784 | 4.5669
20 | Jabalpur | Madhya Pradesh | Central | DRTB Female | DR TB Wards | 50 | 22 | 12.8 | 1100 | 14080 | 398.7012 | 4.7844
20 | Jabalpur | Madhya Pradesh | Central | DRTB Male | DR TB Wards | 50 | 22 | 12.8 | 1100 | 14080 | 398.7012 | 4.7844
20 | Jabalpur | Madhya Pradesh | Central | TB OPD | OPD/ Waiting area | 13 | 12.5 | 13 | 162.5 | 2112.5 | 59.8193 | 0.71783
20 | Jabalpur | Madhya Pradesh | Central | Bronchoscopy Room | Bronchoscopy | 21.4 | 15.3 | 13 | 327.42 | 4256.46 | 120.5295 | 1.4464
21 | Sagar | Madhya Pradesh | Central | chest OPD_1 | OPD/ Waiting area | 19.5 | 13 | 10.8 | 253.5 | 2737.8 | 77.5259 | 0.93031
21 | Sagar | Madhya Pradesh | Central | Broncoscopy | Bronchoscopy | 20.3 | 13.4 | 10.8 | 272.02 | 2937.816 | 83.1897 | 0.99828
21 | Sagar | Madhya Pradesh | Central | OPD waiting Area | OPD/ Waiting area | 26 | 18.2 | 10.8 | 473.2 | 5110.56 | 144.7149 | 1.7366
21 | Sagar | Madhya Pradesh | Central | DRTB WARD (FeMale+Male) | DR TB Wards | 39 | 27.2 | 10.8 | 1060.8 | 11456.64 | 324.4159 | 3.893
21 | Sagar | Madhya Pradesh | Central | DSTB WARD (Female+male) | DS TB Wards | 83 | 35 | 10.8 | 2905 | 31374 | 888.4127 | 10.661
22 | Rewa | Madhya Pradesh | Central | chest OPD | OPD/ Waiting area | 23 | 18.6 | 11.2 | 427.8 | 4791.36 | 135.6762 | 1.6281
22 | Rewa | Madhya Pradesh | Central | Medicine OPD | OPD/ Waiting area | 22 | 19 | 11.2 | 418 | 4681.6 | 132.5681 | 1.5908
22 | Rewa | Madhya Pradesh | Central | DSTB WARD (male +Female) | DS TB Wards | 57 | 22.4 | 10.5 | 1276.8 | 13406.4 | 379.627 | 4.5555
22 | Rewa | Madhya Pradesh | Central | DRTB WARD (FeMale) | DR TB Wards | 18.1 | 22.4 | 10.5 | 405.44 | 4257.12 | 120.5482 | 1.4466
22 | Rewa | Madhya Pradesh | Central | DRTB WARD (Male) | DR TB Wards | 17.7 | 22.4 | 10.5 | 396.48 | 4163.04 | 117.8842 | 1.4146 | 32 | 24 | 34 |  |  |  | 100
** The bidders should provide combinations of two or more fixtures of which one should be < 0.5 W and other fixture/s being > 0.5 W (up to 1.5 W) to match with the total volumetric dose requirement (As mentioned in the column M of the Annexure) in respective areas where they will be installed. Kindly ensure that the total proposed volumetric dosing should not vary +/- 15% from the required volumetric dosing (as per Colum M) as detailed in the schedule-wise annexures.