## Sch 4_South
Sl. No. | Name of DRTB centre | State | Zone | Different sections of the DRTB centre (as written in checklist) | Updated Section labels | Facility Length (in feet) | Facility Width (in feet) | Facility Height (in feet) | Total facility area (in sqft) | Total facility volume (in cubic feet) | Total facility volume (in cubic meter) | Total volumetric doses (12mW/m3) (in Watt) | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Total no of fixtures proposed (T=N+O+P+Q+R+S) | Remarks
1 | GHCCD Vizag | Andhra Pradesh | South | Bronchoscopy Unit | Bronchoscopy | 18.5 | 18.8 | 10.6 | 347.8 | 3686.68 | 104.3952 | 1.2527 | [6 empty] | 0
2 | GHCCD/ IDH), Guntur | Andhra Pradesh | South | DRTB Ward (Male) | DR TB Wards | 28 | 22 | 11.5 | 616 | 7084 | 200.5965 | 2.4072 | [6 empty] | 0
3 | GMC, Trivandrum | Kerala | South | Bronchoscopy Unit | Bronchoscopy | 30 | 20 | 10 | 600 | 6000 | 169.9011 | 2.0388 | [6 empty] | 0
4 | Govt Med Col Kozhikode | Kerala | South | Bronchoscopy Unit-1 | Bronchoscopy | 19.7 | 11 | 9.7 | 216.7 | 2101.99 | 59.5217 | 0.71426 | [6 empty] | 0
4 | Govt Med Col Kozhikode | Kerala | South | Bronchoscopy Unit-2 | Bronchoscopy | 16.8 | 22.7 | 8.7 | 381.36 | 3317.832 | 93.9505 | 1.1274 | [6 empty] | 0
5 | Coimbatore Medical College Hospital, Coimbatore | Tamil Nadu | South | X-RAY WAITING AREA | Radiology waiting area | 50 | 11 | 15 | 550 | 8250 | 233.614 | 2.8034 | [6 empty] | 0
5 | Coimbatore Medical College Hospital, Coimbatore | Tamil Nadu | South | TB OPD | OPD/ Waiting area | 24 | 20 | 11.825 | 480 | 5676 | 160.7264 | 1.9287 | [6 empty] | 0
5 | Coimbatore Medical College Hospital, Coimbatore | Tamil Nadu | South | Bronchoscopy | Bronchoscopy | 22 | 10 | 13 | 220 | 2860 | 80.9862 | 0.97183 | [6 empty] | 0
6 | Rajaji Govt Hospital & MMC, Madurai | Tamil Nadu | South | DRTB WARD | DR TB Wards | 18.5 | 18.5 | 11.2 | 342.25 | 3833.2 | 108.5441 | 1.3025 | [6 empty] | 0
6 | Rajaji Govt Hospital & MMC, Madurai | Tamil Nadu | South | DSTB WARD | DS TB Wards | 35.9 | 17.85 | 11.2 | 640.815 | 7177.128 | 203.2336 | 2.4388 | [6 empty] | 0
6 | Rajaji Govt Hospital & MMC, Madurai | Tamil Nadu | South | DRTB WARD Corridor | DR TB Wards | 39.9 | 8.6 | 10.3 | 343.14 | 3534.342 | 100.0814 | 1.201 | [6 empty] | 0
7 | Thanjavur Medical college,Thanjavur | Tamil Nadu | South | MALE DRTB WARD | DR TB Wards | 28.6 | 24.4 | 10.29 | 697.84 | 7180.7736 | 203.3369 | 2.44 | [6 empty] | 0
7 | Thanjavur Medical college,Thanjavur | Tamil Nadu | South | FEMALE DRTB WARD | DR TB Wards | 28.6 | 24.4 | 10.29 | 697.84 | 7180.7736 | 203.3369 | 2.44 | [6 empty] | 0
8 | Tirunelveli Medical College and TB & Chest Hospital, Tirunelveli | Tamil Nadu | South | TB & C F WARD | DS TB Wards | 19.2 | 10.8 | 11.28 | 207.36 | 2339.0208 | 66.2337 | 0.7948 | [6 empty] | 0
8 | Tirunelveli Medical College and TB & Chest Hospital, Tirunelveli | Tamil Nadu | South | DRTBF WARD | DR TB Wards | 18 | 17.5 | 11 | 315 | 3465 | 98.1179 | 1.1774 | [6 empty] | 0
8 | Tirunelveli Medical College and TB & Chest Hospital, Tirunelveli | Tamil Nadu | South | DRTBM WARD | DR TB Wards | 35 | 17.5 | 11 | 612.5 | 6737.5 | 190.7848 | 2.2894 | [6 empty] | 0
8 | Tirunelveli Medical College and TB & Chest Hospital, Tirunelveli | Tamil Nadu | South | TB & C M WARD | DS TB Wards | 32.9 | 17.9 | 11 | 588.91 | 6478.01 | 183.4368 | 2.2012 | [6 empty] | 0
9 | Government Chest Hospital - Erragadda, Hyderabad | Telangana | South | Female ward | DR TB Wards | 37 | 29 | 9.6 | 1073 | 10300.8 | 291.6862 | 3.5002 | [6 empty] | 0
9 | Government Chest Hospital - Erragadda, Hyderabad | Telangana | South | HIV+ TB ward | DS TB Wards | 94 | 21 | 9.3 | 1974 | 18358.2 | 519.8463 | 6.2382 | [6 empty] | 0
10 | GGH, Eluru | Andhra pradesh | South | DTRB WARD | DR TB Wards | 22.85 | 18.85 | 12.13 | 430.7225 | 5224.6639 | 147.946 | 1.7754 | [6 empty] | 0
11 | GGH, Kakinada | Andhra pradesh | South | Male DTRB WARD | DR TB Wards | 46 | 36 | 12.4 | 1656 | 20534.4 | 581.4695 | 6.9776 | [6 empty] | 0
11 | GGH, Kakinada | Andhra pradesh | South | Female DTRB WARD | DR TB Wards | 46 | 36 | 11.55 | 1656 | 19126.8 | 541.6107 | 6.4993 | [6 empty] | 0
12 | GMCH, Nalgonda | Telangana | South | Commn Pulmonology WARD | DR TB Wards | 56.5 | 18.7 | 11.15 | 1056.55 | 11780.5325 | 333.5875 | 4.0031 | [6 empty] | 0
13 | Nizamabad | Telangana | South | DRTB Ward | DR TB Wards | 35.25 | 21 | 11.3 | 740.25 | 8364.825 | 236.8655 | 2.8424 | [6 empty] | 0
13 | Nizamabad | Telangana | South | DSTB Ward | DS TB Wards | 35.25 | 21 | 11.3 | 740.25 | 8364.825 | 236.8655 | 2.8424 | [6 empty] | 0
14 | Puducherry | Puducherry | South | DSTB Ward A (Male) part_1 | DS TB Wards | 54.7 | 32.8 | 11 | 1794.16 | 19735.76 | 558.8545 | 6.7063 | [6 empty] | 0
14 | Puducherry | Puducherry | South | DSTB Ward A (Male) part_2 | DS TB Wards | 54.7 | 32.8 | 11 | 1794.16 | 19735.76 | 558.8545 | 6.7063 | [6 empty] | 0
14 | Puducherry | Puducherry | South | DSTB Ward B (Male) part_1 | DS TB Wards | 54.7 | 32.8 | 11 | 1794.16 | 19735.76 | 558.8545 | 6.7063 | [6 empty] | 0
14 | Puducherry | Puducherry | South | DSTB Ward B (Male) part_2 | DS TB Wards | 54.7 | 32.8 | 11 | 1794.16 | 19735.76 | 558.8545 | 6.7063 | [6 empty] | 0
14 | Puducherry | Puducherry | South | DSTB Ward C (Female) part_1 | DS TB Wards | 54.7 | 32.8 | 11 | 1794.16 | 19735.76 | 558.8545 | 6.7063 | [6 empty] | 0
15 | KIMS Hubli | Karnataka | South | DSTB ward | DS TB Wards | 18.9 | 12 | 14.3 | 226.8 | 3243.24 | 91.8383 | 1.1021 | [6 empty] | 0
15 | KIMS Hubli | Karnataka | South | OPD | OPD/ Waiting area | 24.9 | 23.8 | 14.4 | 592.62 | 8533.728 | 241.6483 | 2.8998 | [6 empty] | 0
15 | KIMS Hubli | Karnataka | South | Radiology corridor cum waiting area | Radiology waiting area | 157.8 | 9.1 | 14.2 | 1435.98 | 20390.916 | 577.4064 | 6.9289 | [6 empty] | 0
16 | Sivaganga | Tamil Nadu | South | DSTB ward | DS TB Wards | 19.2 | 19.3 | 10 | 370.56 | 3705.6 | 104.9309 | 1.2592 | [6 empty] | 0
16 | Sivaganga | Tamil Nadu | South | OPD | OPD/ Waiting area | 19.3 | 30.7 | 10 | 592.51 | 5925.1 | 167.7801 | 2.0134 | [6 empty] | 0
16 | Sivaganga | Tamil Nadu | South | Medicine OPD | OPD/ Waiting area | 29.1 | 29.3 | 10.4 | 852.63 | 8867.352 | 251.0954 | 3.0131 | [6 empty] | 0
16 | Sivaganga | Tamil Nadu | South | Registration waiting area | Registration/ waiting area | 40 | 29 | 10.4 | 1160 | 12064 | 341.6144 | 4.0994 | [6 empty] | 0
17 | Tumakuru | Karnataka | South | Male DRTB Ward | DR TB Wards | 29.4 | 25.08 | 10.6 | 737.352 | 7815.9312 | 221.3225 | 2.6559 | [6 empty] | 0
17 | Tumakuru | Karnataka | South | Female DRTB Ward | DR TB Wards | 33.5 | 18.8 | 10.6 | 629.8 | 6675.88 | 189.0399 | 2.2685 | [6 empty] | 0
17 | Tumakuru | Karnataka | South | Chest OPD Waiting Area | OPD/ Waiting area | 97 | 7.5 | 11.8 | 727.5 | 8584.5 | 243.086 | 2.917 | [6 empty] | 0
17 | Tumakuru | Karnataka | South | ART Waiting Area | Other | 57.4 | 6.9 | 11.8 | 396.06 | 4673.508 | 132.339 | 1.5881 | [6 empty] | 0
18 | Bengaluru | Karnataka | South | DRTB Ward Male | DR TB Wards | 81.5 | 20 | 11.7 | 1630 | 19071 | 540.0306 | 6.4804 | [6 empty] | 0
18 | Bengaluru | Karnataka | South | DSTB Ward Male | DS TB Wards | 81.5 | 20 | 11.7 | 1630 | 19071 | 540.0306 | 6.4804 | [6 empty] | 0
18 | Bengaluru | Karnataka | South | DSTB Ward Female | DS TB Wards | 81.5 | 20 | 11.7 | 1630 | 19071 | 540.0306 | 6.4804 | [6 empty] | 0
18 | Bengaluru | Karnataka | South | Emergency TB Combined Ward | DR TB Wards | 81.5 | 20 | 11.7 | 1630 | 19071 | 540.0306 | 6.4804 | [6 empty] | 0
18 | Bengaluru | Karnataka | South | CTVS OPD | OPD/ Waiting area | 21.4 | 10.3 | 11.3 | 220.42 | 2490.746 | 70.5301 | 0.84636 | [6 empty] | 0
18 | Bengaluru | Karnataka | South | X-Ray Waiting Area | Radiology waiting area | 108.07 | 10.3 | 11.4 | 1113.121 | 12689.5794 | 359.3289 | 4.3119 | [6 empty] | 0
19 | Gulbarga | Karnataka | South | DTRB male Ward | DR TB Wards | 44 | 20 | 9.7 | 880 | 8536 | 241.7126 | 2.9006 | [6 empty] | 0
19 | Gulbarga | Karnataka | South | DRTB Female Ward | DR TB Wards | 44 | 20 | 9.7 | 880 | 8536 | 241.7126 | 2.9006 | [6 empty] | 0
19 | Gulbarga | Karnataka | South | Exisitng TB OPD | OPD/ Waiting area | 14 | 12.3 | 12.3 | 172.2 | 2118.06 | 59.9768 | 0.71972 | [6 empty] | 0
20 | Raichur | Karnataka | South | DTRB male Ward | DR TB Wards | 21 | 20 | 12.3 | 420 | 5166 | 146.2848 | 1.7554 | [6 empty] | 0
20 | Raichur | Karnataka | South | DRTB Female Ward | DR TB Wards | 49 | 20 | 12.3 | 980 | 12054 | 341.3313 | 4.096 | [6 empty] | 0
20 | Raichur | Karnataka | South | Exisitng TB OPD | OPD/ Waiting area | 14 | 11.4 | 12.3 | 159.6 | 1963.08 | 55.5882 | 0.66706 | [6 empty] | 0
20 | Raichur | Karnataka | South | DSTB ward | DSTB/ Waiting area | 59 | 19.7 | 12 | 1162.3 | 13947.6 | 394.952 | 4.7394 | [6 empty] | 0
21 | Manglore | Karnataka | South | DRTB Male Ward | DR TB Wards | 35.7 | 20.5 | 11.7 | 731.85 | 8562.645 | 242.4671 | 2.9096 | [6 empty] | 0
21 | Manglore | Karnataka | South | DRTB Female Ward | DR TB Wards | 22.8 | 19.9 | 11.7 | 453.72 | 5308.524 | 150.3207 | 1.8038 | [6 empty] | 0
21 | Manglore | Karnataka | South | TB OPD Waiting Area Corridor | OPD/ Waiting area | 76 | 9.4 | 11.7 | 714.4 | 8358.48 | 236.6858 | 2.8402 | [6 empty] | 0
22 | Shimoga | Karnataka | South | DRTB Male & Female Ward | DR TB Wards | 21.5 | 20.4 | 11.5 | 438.6 | 5043.9 | 142.8273 | 1.7139 | [6 empty] | 0
22 | Shimoga | Karnataka | South | DSTB Male Ward | DS TB Wards | 31.7 | 11.2 | 11.5 | 355.04 | 4082.96 | 115.6166 | 1.3874 | [6 empty] | 0
23 | Belagavi | Karnataka | South | DRTB Male Ward | DR TB Wards | 20.3 | 15.1 | 10.4 | 306.53 | 3187.912 | 90.2716 | 1.0833 | [6 empty] | 0
23 | Belagavi | Karnataka | South | DRTB Female Ward | DR TB Wards | 23.7 | 15.1 | 10.5 | 357.87 | 3757.635 | 106.4044 | 1.2769 | [6 empty] | 0
23 | Belagavi | Karnataka | South | DSTB Male Ward | DS TB Wards | 23 | 20.3 | 10.5 | 466.9 | 4902.45 | 138.8219 | 1.6659 | [6 empty] | 0
23 | Belagavi | Karnataka | South | DSTB Female Ward | DR TB Wards | 31.5 | 20 | 10.5 | 630 | 6615 | 187.3159 | 2.2478 | [6 empty] | 0
24 | Hassan | Karnataka | South | Broncoscopy | Bronchoscopy | 19 | 19 | 12.8 | 361 | 4620.8 | 130.8465 | 1.5702 | [6 empty] | 0
24 | Hassan | Karnataka | South | DSTB WARD (FeMale) | DS TB Wards | 63 | 19.6 | 12.4 | 1234.8 | 15311.52 | 433.574 | 5.2029 | [6 empty] | 0
24 | Hassan | Karnataka | South | DSTB WARD (Male) | DS TB Wards | 63 | 19.9 | 12.4 | 1253.7 | 15545.88 | 440.2103 | 5.2825 | [6 empty] | 0
24 | Hassan | Karnataka | South | DRTB WARD (male) | DR TB Wards | 29 | 18.6 | 12.4 | 539.4 | 6688.56 | 189.3989 | 2.2728 | [6 empty] | 0
24 | Hassan | Karnataka | South | DRTB WARD (Female) | DR TB Wards | 19.6 | 19 | 12.4 | 372.4 | 4617.76 | 130.7604 | 1.5691 | [6 empty] | 0
24 | Hassan | Karnataka | South | Medicine OPD | OPD/ Waiting area | 19.8 | 9.1 | 12.4 | 180.18 | 2234.232 | 63.2664 | 0.7592 | [6 empty] | 0
24 | Hassan | Karnataka | South | OPD waiting Area | OPD/ Waiting area | 49 | 8 | 12.4 | 392 | 4860.8 | 137.6425 | 1.6517 | [6 empty] | 0
25 | Mysore | Karnataka | South | Broncoscopy | Bronchoscopy | 21.6 | 14.8 | 14.2 | 319.68 | 4539.456 | 128.5431 | 1.5425 | [6 empty] | 0
25 | Mysore | Karnataka | South | Thoroscopy | Other | 23 | 15 | 14.2 | 345 | 4899 | 138.7242 | 1.6647 | [6 empty] | 0
25 | Mysore | Karnataka | South | DSTB WARD (Female) | DS TB Wards | 42 | 20 | 10.62 | 840 | 8920.8 | 252.6089 | 3.0313 | [6 empty] | 0
25 | Mysore | Karnataka | South | DSTB WARD (male) | DS TB Wards | 42 | 20 | 10.62 | 840 | 8920.8 | 252.6089 | 3.0313 | [6 empty] | 0
** The bidders should provide combinations of two or more fixtures of which one should be < 0.5 W and other fixture/s being > 0.5 W (but not more than 1 W)) to match with the total volumetric dose requirement (As mentioned in the column M of the Annexure) in respective areas where they will be installed. Kindly ensure that the total proposed volumetric dosing should not vary +/- 15% from the required volumetric dosing (as per Colum M) as detailed in the schedule-wise annexures.