## Sch 5_UP+UK & West
Sl. No. | Name of DRTB centre | State | Zone | Different sections of the DRTB centre (as written in checklist) | Updated Section labels | Facility Length (in feet) | Facility Width (in feet) | Facility Height (in feet) | Total facility area (in sqft) | Total facility volume (in cubic feet) | Total facility volume (in cubic meter) | Total volumetric doses (12mW/m3) (in Watt) | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Fixture output (_____) Number | Total no of fixtures proposed (T=N+O+P+Q+R+S) | Remarks
1 | BJ Medical College, Ahemdabad | Gujarat | West | TB Suspect Ward | DS TB Wards | 42.9 | 20.8 | 11.4 | 892.32 | 10172.448 | 288.0516 | 3.4566 | [6 empty] | 0
1 | BJ Medical College, Ahemdabad | Gujarat | West | Bronchoscopy room | Bronchoscopy | 20.6 | 13.7 | 11.5 | 282.22 | 3245.53 | 91.9032 | 1.1028 | [6 empty] | 0
2 | GMERS Medical College, Patan | Gujarat | West | DSTB Male & Female Ward | DS TB Wards | 75.2 | 62.2 | 11.3 | 4677.44 | 52855.072 | 1496.689 | 17.9603 | [6 empty] | 0
3 | Sayaji Rao Shinde Government Hospital, Vadodara | Gujarat | West | Bronchoscopy Suite | Bronchoscopy | 19.3 | 18.8 | 14.2 | 362.84 | 5152.328 | 145.8977 | 1.7508 | [6 empty] | 0
3 | Sayaji Rao Shinde Government Hospital, Vadodara | Gujarat | West | DRTB Male & Female Ward | DR TB Wards | 57 | 38.9 | 11.8 | 2217.3 | 26164.14 | 740.8859 | 8.8906 | [6 empty] | 0
3 | Sayaji Rao Shinde Government Hospital, Vadodara | Gujarat | West | DSTB Male & Female Ward | DS TB Wards | 58.2 | 44.6 | 11.8 | 2595.72 | 30629.496 | 867.3307 | 10.408 | [6 empty] | 0
4 | Government Medical College, Miraj | Maharashtra | West | DRTB ward (male) | DR TB Wards | 37.1 | 20.3 | 10.9 | 753.13 | 8209.117 | 232.4563 | 2.7895 | [6 empty] | 0
4 | Government Medical College, Miraj | Maharashtra | West | OPD1 | OPD/ Waiting area | 34.5 | 24.5 | 10.9 | 845.25 | 9213.225 | 260.8895 | 3.1307 | [6 empty] | 0
4 | Government Medical College, Miraj | Maharashtra | West | DRTB ward (Female) | DR TB Wards | 36.8 | 28.5 | 10.9 | 1048.8 | 11431.92 | 323.7159 | 3.8846 | [6 empty] | 0
4 | Government Medical College, Miraj | Maharashtra | West | Waiting area for Registration | Registration/ waiting area | 26.1 | 23.1 | 10.7 | 602.91 | 6451.137 | 182.6759 | 2.1921 | [6 empty] | 0
4 | Government Medical College, Miraj | Maharashtra | West | Registration Room | Registration/ waiting area | 24.4 | 10.8 | 10.7 | 263.52 | 2819.664 | 79.844 | 0.95813 | [6 empty] | 0
5 | Government Medical College, Nagpur | Maharashtra | West | DSTB Ward | DS TB Wards | 79.7 | 20.3 | 10.4 | 1617.91 | 16826.264 | 476.4667 | 5.7176 | [6 empty] | 0
6 | Rajiv Gandhi Medical College, Thane | Maharashtra | West | DRTB Ward (Male) | DR TB Wards | 43 | 30 | 12.93 | 1290 | 16679.7 | 472.3165 | 5.6678 | [6 empty] | 0
6 | Rajiv Gandhi Medical College, Thane | Maharashtra | West | DRTB Ward (Female) | DR TB Wards | 43 | 21 | 12.93 | 903 | 11675.79 | 330.6216 | 3.9675 | [6 empty] | 0
7 | Baba Raghav Das medical college, Gorakhpur | Uttar Pradesh | UP+UK | DRTB Female Ward | DR TB Wards | 22 | 15.8 | 10.9 | 347.6 | 3788.84 | 107.288 | 1.2875 | [6 empty] | 0
7 | Baba Raghav Das medical college, Gorakhpur | Uttar Pradesh | UP+UK | DRTB Male Ward | DR TB Wards | 22 | 15.8 | 10.9 | 347.6 | 3788.84 | 107.288 | 1.2875 | [6 empty] | 0
7 | Baba Raghav Das medical college, Gorakhpur | Uttar Pradesh | UP+UK | OPD Waiting Area | OPD/ Waiting area | 26.8 | 21.6 | 10.8 | 578.88 | 6251.904 | 177.0342 | 2.1244 | [6 empty] | 0
8 | BHU, Varanasi | Uttar Pradesh | UP+UK | OPD 2 | OPD/ Waiting area | 12 | 12 | 10 | 144 | 1440 | 40.7763 | 0.48932 | [6 empty] | 0
8 | BHU, Varanasi | Uttar Pradesh | UP+UK | MALE DRTB WARD | DR TB Wards | 40 | 23 | 11 | 920 | 10120 | 286.5665 | 3.4388 | [6 empty] | 0
8 | BHU, Varanasi | Uttar Pradesh | UP+UK | FEMALE DRTB WARD | DR TB Wards | 40 | 23 | 11 | 920 | 10120 | 286.5665 | 3.4388 | [6 empty] | 0
8 | BHU, Varanasi | Uttar Pradesh | UP+UK | Registration Waiting Area | Registration/ waiting area | 45 | 24 | 9 | 1080 | 9720 | 275.2397 | 3.3029 | [6 empty] | 0
8 | BHU, Varanasi | Uttar Pradesh | UP+UK | Bronchoscopy Room | Bronchoscopy | 14 | 12 | 11 | 168 | 1848 | 52.3295 | 0.62795 | [6 empty] | 0
8 | BHU, Varanasi | Uttar Pradesh | UP+UK | OPD 1 | OPD/ Waiting area | 24 | 11 | 11 | 264 | 2904 | 82.2321 | 0.98679 | [6 empty] | 0
9 | Deen Dayal Upadhyay District Hospital, Moradabad | Uttar Pradesh | UP+UK | Female Ward | DR TB Wards | 23.6 | 21.5 | 13 | 507.4 | 6596.2 | 186.7836 | 2.2414 | [6 empty] | 0
9 | Deen Dayal Upadhyay District Hospital, Moradabad | Uttar Pradesh | UP+UK | Male Ward | DR TB Wards | 23 | 21 | 13 | 483 | 6279 | 177.8015 | 2.1336 | [6 empty] | 0
10 | Dr. Murari Lal Chest Hospital, Kanpur | Uttar Pradesh | UP+UK | OPD (TB +General chest )-1 | OPD/ Waiting area | 14.5 | 21 | 13 | 304.5 | 3958.5 | 112.0922 | 1.3451 | [6 empty] | 0
10 | Dr. Murari Lal Chest Hospital, Kanpur | Uttar Pradesh | UP+UK | DRTB (male) | DR TB Wards | 50 | 21 | 13 | 1050 | 13650 | 386.525 | 4.6383 | [6 empty] | 0
10 | Dr. Murari Lal Chest Hospital, Kanpur | Uttar Pradesh | UP+UK | DRTB (female) | DR TB Wards | 50 | 21 | 13 | 1050 | 13650 | 386.525 | 4.6383 | [6 empty] | 0
10 | Dr. Murari Lal Chest Hospital, Kanpur | Uttar Pradesh | UP+UK | OPD (TB +General chest )-2 | OPD/ Waiting area | 14.5 | 22.5 | 13 | 326.25 | 4241.25 | 120.0988 | 1.4412 | [6 empty] | 0
11 | JNMC & Hospital, Aligarh | Uttar Pradesh | UP+UK | Demontration Centre OPD (TB OPD) | OPD/ Waiting area | 21.6 | 20.7 | 8.9 | 447.12 | 3979.368 | 112.6832 | 1.3522 | [6 empty] | 0
11 | JNMC & Hospital, Aligarh | Uttar Pradesh | UP+UK | MALE DRTB WARD | DR TB Wards | 27 | 19.9 | 9.5 | 537.3 | 5104.35 | 144.5391 | 1.7345 | [6 empty] | 0
11 | JNMC & Hospital, Aligarh | Uttar Pradesh | UP+UK | FEMALE DRTB WARD | DR TB Wards | 27 | 19.7 | 9.5 | 531.9 | 5053.05 | 143.0864 | 1.717 | [6 empty] | 0
12 | King George's Medical University Nodal TB centre Lucknow | Uttar Pradesh | UP+UK | DRTB (male) | DR TB Wards | 17.8 | 40 | 11.78 | 712 | 8387.36 | 237.5036 | 2.85 | [6 empty] | 0
12 | King George's Medical University Nodal TB centre Lucknow | Uttar Pradesh | UP+UK | DRTB (female) | DR TB Wards | 17.8 | 40 | 11.78 | 712 | 8387.36 | 237.5036 | 2.85 | [6 empty] | 0
12 | King George's Medical University Nodal TB centre Lucknow | Uttar Pradesh | UP+UK | OPD -1 | OPD/ Waiting area | 25 | 16 | 13.89 | 400 | 5556 | 157.3284 | 1.8879 | [6 empty] | 0
12 | King George's Medical University Nodal TB centre Lucknow | Uttar Pradesh | UP+UK | Bronchoscopy | Bronchoscopy | 28.6 | 11.6 | 10.1 | 331.76 | 3350.776 | 94.8834 | 1.1386 | [6 empty] | 0
13 | Lala Lajpat Rai Memorial Medical College, Meerut | Uttar Pradesh | UP+UK | 4th floor female ward 1 DRTB | DR TB Wards | 25.56 | 21 | 11.2 | 536.76 | 6011.712 | 170.2327 | 2.0428 | [6 empty] | 0
13 | Lala Lajpat Rai Memorial Medical College, Meerut | Uttar Pradesh | UP+UK | 4th floor male ward 1 DRTB | DR TB Wards | 25 | 21 | 11.2 | 525 | 5880 | 166.5031 | 1.998 | [6 empty] | 0
13 | Lala Lajpat Rai Memorial Medical College, Meerut | Uttar Pradesh | UP+UK | OPD waiting area | OPD/ Waiting area | 118 | 10 | 11 | 1180 | 12980 | 367.5527 | 4.4106 | [6 empty] | 0
13 | Lala Lajpat Rai Memorial Medical College, Meerut | Uttar Pradesh | UP+UK | Registration area (F) | Registration/ waiting area | 21 | 28 | 11 | 588 | 6468 | 183.1534 | 2.1978 | [6 empty] | 0
14 | Maharana Pratap District Hospital Bareilly | Uttar Pradesh | UP+UK | DRTB Ward (Female) | DR TB Wards | 20 | 22 | 11.5 | 440 | 5060 | 143.2832 | 1.7194 | [6 empty] | 0
14 | Maharana Pratap District Hospital Bareilly | Uttar Pradesh | UP+UK | DSTB Ward | DS TB Wards | 20 | 22 | 11.5 | 440 | 5060 | 143.2832 | 1.7194 | [6 empty] | 0
14 | Maharana Pratap District Hospital Bareilly | Uttar Pradesh | UP+UK | OPD Waiting area | RADIOLOGY WAITING AREA | 60 | 12 | 13.8 | 720 | 9936 | 281.3562 | 3.3763 | [6 empty] | 0
14 | Maharana Pratap District Hospital Bareilly | Uttar Pradesh | UP+UK | DRTB Ward (Male) | DR TB Wards | 22 | 40 | 11.5 | 880 | 10120 | 286.5665 | 3.4388 | [6 empty] | 0
15 | Maharani Laxmibai Medical College, Jhansi | Uttar Pradesh | UP+UK | FEMALE DRTB WARD | DR TB Wards | 18.8 | 19.49 | 11.68 | 366.412 | 4279.6922 | 121.1874 | 1.4542 | [6 empty] | 0
15 | Maharani Laxmibai Medical College, Jhansi | Uttar Pradesh | UP+UK | MALE DRTB WARD | DR TB Wards | 46 | 19.49 | 11.68 | 896.54 | 10471.5872 | 296.5223 | 3.5583 | [6 empty] | 0
16 | Saifai medical college, Etawah | Uttar Pradesh | UP+UK | New Proposed DRTB Male/Female ward & TB-LAB | DR TB Wards | 63.8 | 19.8 | 11.2 | 1263.24 | 14148.288 | 400.6349 | 4.8076 | [6 empty] | 0
17 | SR HOSPITAL, MLN MC, PRAYAGRAJ | Uttar Pradesh | UP+UK | DSTB WARD | DS TB Wards | 25.2 | 21.2 | 11 | 534.24 | 5876.64 | 166.4079 | 1.9969 | [6 empty] | 0
17 | SR HOSPITAL, MLN MC, PRAYAGRAJ | Uttar Pradesh | UP+UK | DRTB WARD | DR TB Wards | 52 | 32.7 | 13.2 | 1700.4 | 22445.28 | 635.5796 | 7.627 | [6 empty] | 0
18 | TB HOSPITAL, TELIYARGANJ | Uttar Pradesh | UP+UK | DSTB WARD MALE | DS TB Wards | 92.9 | 46.4 | 17.7 | 4310.56 | 76296.912 | 2160.488 | 25.9259 | [6 empty] | 0
18 | TB HOSPITAL, TELIYARGANJ | Uttar Pradesh | UP+UK | DSTB WARD FEMALE | DS TB Wards | 108.2 | 33.8 | 13.7 | 3657.16 | 50103.092 | 1418.7616 | 17.0251 | [6 empty] | 0
18 | TB HOSPITAL, TELIYARGANJ | Uttar Pradesh | UP+UK | DRTB WARD | DR TB Wards | 83.5 | 18.9 | 13.9 | 1578.15 | 21936.285 | 621.1664 | 7.454 | [6 empty] | 0
19 | Doon Medical College, Dehradun | Uttarakhand | UP+UK | DRTB Ward | DR TB Wards | 44 | 14 | 8.7 | 616 | 5359.2 | 151.7556 | 1.8211 | [6 empty] | 0
19 | Doon Medical College, Dehradun | Uttarakhand | UP+UK | Female Ward | DR TB Wards | 26 | 23 | 9.4 | 598 | 5621.2 | 159.1747 | 1.9101 | [6 empty] | 0
19 | Doon Medical College, Dehradun | Uttarakhand | UP+UK | Positive Male ward | DR TB Wards | 26 | 26 | 9.4 | 676 | 6354.4 | 179.9366 | 2.1592 | [6 empty] | 0
19 | Doon Medical College, Dehradun | Uttarakhand | UP+UK | DSTB Ward | DS TB Wards | 43 | 17 | 9.7 | 731 | 7090.7 | 200.7863 | 2.4094 | [6 empty] | 0
19 | Doon Medical College, Dehradun | Uttarakhand | UP+UK | Broncoscopy | Bronchoscopy | 17 | 9.2 | 9.7 | 156.4 | 1517.08 | 42.9589 | 0.51551 | [6 empty] | 0
20 | Kachchh | Gujarat | West | DS-TB ward male | DS TB Wards | 31.3 | 20.6 | 10.9 | 644.78 | 7028.102 | 199.0137 | 2.3882 | [6 empty] | 0
21 | Unnao | Uttar Pradesh | UP+UK | TB OPD (DH) | OPD/ Waiting area | 15.8 | 10.4 | 11 | 164.32 | 1807.52 | 51.1833 | 0.6142 | [6 empty] | 0
21 | Unnao | Uttar Pradesh | UP+UK | Waiting Area Radiology (DH) | Radiology | 23.5 | 9.6 | 11.5 | 225.6 | 2594.4 | 73.4652 | 0.88158 | [6 empty] | 0
21 | Unnao | Uttar Pradesh | UP+UK | DRTB Ward (DH) | DR TB Wards | 22.3 | 21.9 | 10.8 | 488.37 | 5274.396 | 149.3543 | 1.7923 | [6 empty] | 0
22 | Amaravati | Maharashtra | West | DRTB Male & Female Ward | DR TB Wards | 44.6 | 15 | 15.5 | 669 | 10369.5 | 293.6315 | 3.5236 | [6 empty] | 0
22 | Amaravati | Maharashtra | West | DSTB Male & Female Ward | DR TB Wards | 101.1 | 20.8 | 13.6 | 2102.88 | 28599.168 | 809.8383 | 9.7181 | [6 empty] | 0
23 | Buldhana | Maharashtra | West | DRTB Male & Female Ward | DR TB Wards | 42 | 30 | 13.6 | 1260 | 17136 | 485.2375 | 5.8228 | [6 empty] | 0
23 | Buldhana | Maharashtra | West | DSTB Male Ward | DS TB Wards | 90 | 20 | 13.7 | 1800 | 24660 | 698.2934 | 8.3795 | [6 empty] | 0
23 | Buldhana | Maharashtra | West | DSTB Female Ward | DS TB Wards | 100 | 21 | 13.7 | 2100 | 28770 | 814.6757 | 9.7761 | [6 empty] | 0
24 | Firozabad | Uttar Pradesh | UP+UK | DRTB Male & Female Ward | DR TB Wards | 27.6 | 23.8 | 17.6 | 656.88 | 11561.088 | 327.3736 | 3.9285 | [6 empty] | 0
24 | Firozabad | Uttar Pradesh | UP+UK | DSTB Male Ward | DS TB Wards | 54.5 | 30 | 18 | 1635 | 29430 | 833.3648 | 10.0004 | [6 empty] | 0
24 | Firozabad | Uttar Pradesh | UP+UK | DSTB Female Ward | DS TB Wards | 23.7 | 17.3 | 10.4 | 410.01 | 4264.104 | 120.746 | 1.449 | [6 empty] | 0
25 | Orai | Uttar Pradesh | UP+UK | DRTB Male & Female Ward | DR TB Wards | 42.4 | 24 | 9.7 | 1017.6 | 9870.72 | 279.5077 | 3.3541 | [6 empty] | 0
25 | Orai | Uttar Pradesh | UP+UK | DSTB Male & Female Ward | DS TB Wards | 48.3 | 20 | 9.7 | 966 | 9370.2 | 265.3345 | 3.184 | [6 empty] | 0
25 | Orai | Uttar Pradesh | UP+UK | TB OPD Waiting Area | OPD/ Waiting area | 72.2 | 30 | 9.8 | 2166 | 21226.8 | 601.076 | 7.2129 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | OPD(0149) | OPD/ Waiting area | 13.9 | 11.8 | 8.7 | 164.02 | 1426.974 | 40.4074 | 0.48489 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | OPD(0150) | OPD/ Waiting area | 13.9 | 11.8 | 8.7 | 164.02 | 1426.974 | 40.4074 | 0.48489 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | DRTB-Female | DR TB Wards | 23 | 12 | 9.2 | 276 | 2539.2 | 71.9021 | 0.86283 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | DRTB-male | DR TB Wards | 25.4 | 24 | 9.2 | 609.6 | 5608.32 | 158.8099 | 1.9057 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | DRTB Ward | DR TB Wards | 21.3 | 12.3 | 9.2 | 261.99 | 2410.308 | 68.2523 | 0.81903 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | DSTB-male | DS TB Wards | 25.4 | 23 | 9.2 | 584.2 | 5374.64 | 152.1929 | 1.8263 | [6 empty] | 0
26 | Greater Noida | Uttar Pradesh | UP+UK | DSTB-Female | DS TB Wards | 25.4 | 11.8 | 9.2 | 299.72 | 2757.424 | 78.0816 | 0.93698 | [6 empty] | 0
27 | HIMS, Jolly Grant, Dehradun | Uttarakhand | UP+UK | DRTB Ward | DR TB Wards | 41 | 21.2 | 11.8 | 869.2 | 10256.56 | 290.4334 | 3.4852 | [6 empty] | 0
27 | HIMS, Jolly Grant, Dehradun | Uttarakhand | UP+UK | Bronchoscopy | Bronchoscopy | 20 | 20 | 9 | 400 | 3600 | 101.9406 | 1.2233 | [6 empty] | 0
27 | HIMS, Jolly Grant, Dehradun | Uttarakhand | UP+UK | Radiology waiting Area | Radiology waiting area | 43 | 20 | 9.2 | 860 | 7912 | 224.0429 | 2.6885 | [6 empty] | 0
28 | Amreli | Gujarat | West | DSTB Male Ward | DS TB Wards | 47 | 39.5 | 11.2 | 1856.5 | 20792.8 | 588.7865 | 7.0654 | [6 empty] | 0
28 | Amreli | Gujarat | West | DSTB Female Ward | DS TB Wards | 43 | 43 | 11.2 | 1849 | 20708.8 | 586.4079 | 7.0369 | [6 empty] | 0
29 | Ahmednagar | Maharashtra | West | DRTB Male & Female Ward | DR TB Wards | 30.4 | 15.1 | 11.8 | 459.04 | 5416.672 | 153.3831 | 1.8406 | [6 empty] | 0
29 | Ahmednagar | Maharashtra | West | DSTB Male & Female Ward | DS TB Wards | 27.8 | 18.9 | 12 | 525.42 | 6305.04 | 178.5389 | 2.1425 | [6 empty] | 0
30 | Kolhapur | Maharashtra | West | DSTB Male & Female Ward Corridor | DS TB Wards | 70 | 8.3 | 14.5 | 581 | 8424.5 | 238.5553 | 2.8627 | [6 empty] | 0
30 | Kolhapur | Maharashtra | West | Pharmacy Distribution | Other | 40 | 16 | 11.7 | 640 | 7488 | 212.0365 | 2.5444 | [6 empty] | 0
** The bidders should provide combinations of two or more fixtures of which one should be < 0.5 W and other fixture/s being > 0.5 W (but not more than 1 W) to match with the total volumetric dose requirement (As mentioned in the column M of the Annexure) in respective areas where they will be installed. Kindly ensure that the total proposed volumetric dosing should not vary +/- 15% from the required volumetric dosing (as per Colum M) as detailed in the schedule-wise annexures.